## Blad1
Various (parameter) settings RfG and Netcode | [6 empty] | v07 -- Oct 2020
Description | RfG art. | Ranges by RfG | Netcode art. | Ranges by Netcode | ONSHORE | OFFSHORE WIND | Remark
Frequency stability
Rate of change of frequency (df/dt) to withstand | RfG 13-1b |  | (NC 3.13/2) | (reserved article) proposal: 2 Hz/s | 2 Hz/s | 2 Hz/s
LFSM-O: Overfrequency threshold | RfG 13-2c | 50,2 - 50,5 Hz | NC 3.13/4b | 50,2 Hz | =NC | =NC
LFSM-O: Overfrequency droop | RfG 13-2d | 2% - 12% | NC 3.13/4c-d | 4% - 12% default: 5% | =NC | =NC | Parameter setting
Upon reaching minimum regulating level | RfG 13-2f | continue at this level or further reduce MW | NC 3.13/4e | continue at this level | =NC | =NC
Admissible active power reduction at falling frequency | RfG 13-4 (Fig. 2) | between <49 Hz, rate 2% and <49,5 Hz, rate 10% | NC 3.13/5 | <49,5 Hz, rate 10% | =NC | =NC
LFSM-U: Underfrequency threshold | RfG 15-2c (i) | 49,8 - 49,5 Hz | NC 3.24/2b | 49,8 Hz | =NC | =NC | Taken into account availability primary energy sources
LFSM-U: Underfrequency droop | RfG 15-2c (i) | 2% - 12% | NC 3.24/2c-d | 4% - 12% default: 5% | =NC | =NC | Parameter setting Taken into account availability primary energy sources
FSM: Parameters for Table 4, Figure 5: -- active power range -- insensitivity -- dead band -- droop | RfG 15-2d (i) | -- 1,5% - 10% -- 10 - 30 mHz -- 0 - 500 mHz -- 2% - 12% | NC 3.24/3 | -- 1,5% - 10% -- 10 mHz -- 0 - 500 mHz -- 4% - 12% | =NC | =NC | Parameter setting Taken into account availability primary energy sources
FSM: Parameters for Table 5, Figure 6: -- active power range -- initial delay t1 (with inertia) -- initial delay t1 (without inertia) -- full activation time t2 | RfG 15-2d (iii) | -- 1,5% - 10% -- <2 s -- by TSO -- <30 s | NC 3.24/4 | =RfG | ATO/CTA | -- =NC -- =NC -- <1 s -- =NC | Parameter setting Taken into account availability primary energy sources
FSM: Specify additional signals | RfG 15-2g (ii) |  |  |  | n.a. | n.a. | Work in progress by TenneT
Specify capability of providing synthetic inertia during very fast frequency deviations | RfG 20-2a |  |  |  | n.a. | n.a. | To be determined by TenneT
Voltage stability
Reactive power control mode | RfG 21-3d (i) | reactive power cos(phi) voltage | NC 3.34/1c | reactive power cos(phi) voltage | reactive power cos(phi) voltage submode1 voltage submode 2 | reactive power cos(phi) voltage submode1 voltage submode 2 | Parameter setting
Voltage droop / slope | RfG 21-3d (ii) | 2% - 7% |  |  | default: 7% | default: 7% | Setting via local HMI
Response time reactive power (MVAr) to 90% | RfG 21-3d (iv) | 1 s < t1 < 5 s | NC 3.26-4 | 1 s < t1 < 5 s | 1 s | 1 s | Parameter setting
Settling time reactive power (MVAr) | RfG 21-3d (iv) | 5 s < t2 < 60 s | NC 3.26-4 | 5 s < t2 < 60 s | 5 s | 5 s | Parameter setting
Maximum overshoot reactive power response | -- |  | -- |  | such that U overshoot <1% | such that U overshoot <1%
Tolerance steady state reactive power | RfG 21-3d (v) | U mode: +/-5% MVAr mode: lowest of +/-5 MVAr and +/-5% |  |  | =RfG | =RfG
Steady state reactive power exchange | -- |  | -- |  | 0 MVAr | +/- 0,1 pu
Tolerance of power factor and time to reach it | RfG 21-3d (vi) |  | -- |  | 5% and 5 s | 5% and 5 s
Fast reactive current injection: droop / default | RfG 20-2b |  | NC 3.33/5f, h | 2 ≤ k ≤ 10 default: k = 2 (5) | =NC | =NC | Parameter setting Netcode is/wil be updated to "5"
Robustness
Fault ride through capability | RfG 14-3 RfG 16-3 | (depends on type A-D and voltage level) | NC 3.17/3 NC 3.28/2-3 | (depends on type A-D and voltage level) | =RfG =NC | =RfG 16-3 =NC 3.17/3
Post-fault active power recovery: -- when to start recovery (voltage criterion) -- max. allowed time -- magnitude -- and accuracy | RfG 20-3a |  |  |  | -- 90% prefault U -- 0,5 < x < 10 s -- 90% prefault P -- accuracy 10% | -- 90% prefault U -- 0,5 < x < 10 s -- 90% prefault P -- accuracy 10% | Also text proposal for Netcode art. 3.19
During fault ride through: priority to active or reactive power | RfG 21-3e |  |  |  | reactive power | reactive power
Specify if PPM shall be capable of damping oscillations | RfG 21-3f |  |  |  | n.a. | n.a.
System management
Active power setpoint sent by TSO: time to reach setpoint | RfG 15-2a |  | NC 3.24/1b | "ATO/CTA" | <15 min | <15 min
Min./max. active power (MW) rates up/down | RfG 15-6e |  | NC 3.24/15 | min. rate up/down: 1% per minute max. rate up/down: 20% per minute | =NC | =NC
Min./max. active power (MW) rate up for recovery after fault | -- |  | -- |  | ?? | ?? | Germany: 10% - 20% per second
Miscellaneous
Flicker: -- PLTi -- PSTi | -- |  | -- |  | -- less or equal 0,25 -- less or equal 0,35 | -- less or equal 0,25 -- less or equal 0,35